## Load range and support distance
Distance between VT-CBC hangers
Ceiling weight kg/m2 | P (mm) | G (mm) | kg/support
10 -15 | 1200 | 900 | 11 - 14
15 -30 | 1000 | 800 | 11 - 22
30 - 50 | 750 | 600 | 13 - 22
50 - 75 | 600 | 600 | 18 - 27
Spacing S should not exceed 400 mm at longitudinal installation and 500 mm at transversal installation.

## Natural frequency & deflection
Type | Elastic part | fn (Hz) | Deflection (mm)
VT-CBC-RF25 | 25 mm pad | 9 - 11 | 1 - 2
VT-CBC-RF37 | 37 mm pad | 7 - 9 | 2 - 3
VT-CBC-RF50 | 50 mm pad | 6 - 7 | 4 - 5